PASA BC POLICY

Version 1.0

DOCUMENT CONTROL:

| REVISION NUMBER | DATE | SECTIONS EFFECTED | DESCRIPTION OF REVISION |
| --- | --- | --- | --- |
| 1.0 | July 2011 | New Document | New Document |

ACCEPTANCE OF THE DOCUMENT

| NAME | DESIGNATION | SIGNATURE | DATE | APPROVE / REJECT / DEFER |
| --- | --- | --- | --- | --- |
| E Esterhuysen | Executive Operations |  | July 2011 | Approved |

PURPOSE OF THE DOCUMENT

Provide a minimum connectivity and infrastructure framework document in order to achieve a viable disaster recovery solution for System Operators (SO).

AUDIENCE:

SO’s separated in two categories:

- Category A – SO who achieve more than 1 million transactions per month

- Category B – SO who achieve less than 1 million transactions per month

OVERVIEW OF PROPOSED DISASTER RECOVERY SOLUTION

A high availability, multi layered secure and scalable network and server infrastructure, distributed over two locations for Category A SO’s, automated failover within a single site for Category B SO’s.

TELECOMMUNICATIONS

- Telecommunications infrastructure (dual provider)

  - Telkom

  - Neotel

  - MTN

  - Vodacom

Listed above are the more well known and wide spread providers in the telecommunications space, which should allow for easier installation dependent on location.

Dual providers will allow for a cheaper alternative to the platinum SLA solution, yet allow route diversity.

Networks Category A – Across Dual sites

- Dual provider entry/exit.

- Dual routers for redundancy.

- Dual switches for redundancy.

- Dual firewalls for redundancy.

- Remove any single point of failure.

Networks Category B – Single site

- Dual provider entry/exit.

- Dual routers for redundancy.

- Dual switches for redundancy.

- Dual firewalls for redundancy.

- Remove any single point of failure.

INFRASTRUCTURE:

Servers – Category A

- Servers enabled with automated failover (cluster)

- Replication between sites

- Dual network cards teamed to alternate switches

- High availability servers which include RAID 5, dual power supplies, dual network cards

Backup – Category A

- Backup environment

- Replication between sites

- Backup critical data and OS

- Backup to tape

- Send tape off site

Servers – Category B

- Servers enabled with automated failover (cluster)

- Dual network cards teamed to alternate switches

- High availability servers which include RAID 5, dual power supplies, dual network cards

Backup – Category B

- Backup environment

- Backup critical data and OS

- Backup to tape

- Send tape off site

COMMUNICATIONS LINKS:

- Clients will ensure adequate service level agreements are in place with the Communications Providers

- Dual lines from clients’ site to SO primary site

- Dual lines from clients’ site to SO secondary site

- Line capacity not to exceed 2MB

- Lines must be split across dual telecom providers, or, full route redundancy must be catered for by the provider.

- Lines are to be split across separate routers to cater for device failure.

FAILOVER:

- HSRP to be enabled on critical and client facing network equipment, for example routers and switches, with firewall failover enabled.

- Router HSRP to provide protocol tracking to ensure successful failover

MONITORING:

- IP SLA to be enabled across the links for monitoring purposes

- IP Addressing for the WAN links to be provided by the client with a /30 mask

- Clients required to monitor link status as well and report faults to the relevant service provider for further action

DR TESTING:

- DR Testing to be completed bi-annually

- Distance of second site to conform to SARB banking recommendations

- Link failover to be tested with each DR test

- Device failover to be tested with each DR test

IP ADDRESSING:

- Clients must supply Public IP addresses to use on Wide Area Network links and to access servers

- Public IP addresses must be registered to clients

- IP Addressing limited to IPv4

NETWORK HARDWARE:

Clients’ network devices must support encryption.